## Sheet1
变量名 | range | rate | default | controller | description | canonical_name | manifest_name | runtime_field | layer | aliases
load_output | [300.0, 400.0] | [-20.0, 20.0] | 349 | LoadInstructionGenerator | 负荷指令生成器最终输出 | load_output | simulation_load_output | load_output | setpoint
steam_setpoint | [18.0, 29.0] | [-1.5, 1.5] | 23.7 | MainSteamPressureController | 主蒸汽压力设定值（限速后最终输出） | steam_setpoint | simulation_steam_setpoint | steam_setpoint | setpoint
boiler_setpoint | [0.0, 250.0] | [-5.0, 5.0] | 157.6 | BoilerMasterController | 锅炉主控PID最终输出 | boiler_setpoint | simulation_boiler_setpoint | boiler_setpoint | setpoint
fuel_command | [0.0, 400.0] | [-5.0, 5.0] | 157.6 | FuelController | 给煤指令最终输出 | fuel_command | simulation_fuel_command | fuel_command | actuator
water_setpoint | [900.0, 1200.0] | [-50.0, 50.0] | 1065.7 | WaterK | 给水流量设定值最终输出 | water_setpoint | simulation_water_setpoint | water_setpoint | setpoint
water_pump_speed | [2000.0, 3000.0] | [-150.0, 150.0] | 2500 | FeedwaterController | 给水泵转速指令最终输出 | water_pump_speed | simulation_water_pump_speed | water_pump_speed | actuator
loadgen_rate_output | [300.0, 400.0] | [-20.0, 20.0] | 349 | LoadInstructionGenerator | 负荷指令速率限制器输出 | loadgen_rate_output | simulation_loadgen_rate_output | loadgen_rate_output | controller_output
steam_hfop1_output | [18.0, 29.0] | [-1.5, 1.5] | 23.7 | MainSteamPressureController | 压力设定值一阶惯性滤波器1输出 | steam_hfop1_output | simulation_steam_hfop1_output | steam_hfop1_output | controller_output
steam_hfop2_output | [18.0, 29.0] | [-1.5, 1.5] | 23.7 | MainSteamPressureController | 压力设定值一阶惯性滤波器2输出 | steam_hfop2_output | simulation_steam_hfop2_output | steam_hfop2_output | controller_output
steam_hfop3_output | [18.0, 29.0] | [-1.5, 1.5] | 23.7 | MainSteamPressureController | 压力设定值一阶惯性滤波器3输出 | steam_hfop3_output | simulation_steam_hfop3_output | steam_hfop3_output | controller_output
steam_hfop4_output | [18.0, 29.0] | [-1.5, 1.5] | 23.7 | MainSteamPressureController | 压力设定值一阶惯性滤波器4输出 | steam_hfop4_output | simulation_steam_hfop4_output | steam_hfop4_output | controller_output
steam_rate_output | [18.0, 29.0] | [-0.5, 0.5] | 23.7 | MainSteamPressureController | 压力设定值速率限制器输出 | steam_rate_output | simulation_steam_rate_output | steam_rate_output | controller_output
boiler_pv_filtered | [18.0, 29.0] | [-1.5, 1.5] | 23.7 | BoilerMasterController | 锅炉主控PV惯性滤波器输出（主蒸汽压力滤波值） | boiler_pv_filtered | simulation_boiler_pv_filtered | boiler_pv_filtered | controller_output
boiler_pid_output | [0.0, 250.0] | [-5.0, 5.0] | 157.6 | BoilerMasterController | 锅炉主控PID输出（手操值） | boiler_pid_output | simulation_boiler_pid_output | boiler_pid_output | controller_output
fuel_rate_output | [0.0, 300.0] | [-10.0, 10.0] | 157.6 | FuelController | 燃料控制速率限制器输出 | fuel_rate_output | simulation_fuel_rate_output | fuel_rate_output | controller_output
fuel_pid_output | [0.0, 300.0] | [-2.0, 2.0] | 157.6 | FuelController | 燃料PID输出（手操值） | fuel_pid_output | simulation_fuel_pid_output | fuel_pid_output | controller_output
fuel_filter_output | [0.0, 300.0] | [-5.0, 5.0] | 157.6 | FuelController | 燃料控制输出滤波器输出 | fuel_filter_output | simulation_fuel_filter_output | fuel_filter_output | controller_output
waterk_filter_output | [900.0, 1200.0] | [-50.0, 50.0] | 1065.7 | WaterK | 给水设定值惯性滤波器输出 | waterk_filter_output | simulation_waterk_filter_output | waterk_filter_output | controller_output
water_pid_output | [0.0, 5000.0] | [-50.0, 50.0] | 2500 | FeedwaterController | 给水PID输出（手操值） | water_pid_output | simulation_water_pid_output | water_pid_output | controller_output
water_rate_output | [0.0, 5000.0] | [-200.0, 200.0] | 2500 | FeedwaterController | 给水泵速率限制器输出 | water_rate_output | simulation_water_rate_output | water_rate_output | controller_output
water_filter_output | [0.0, 5000.0] | [-150.0, 150.0] | 2500 | FeedwaterController | 给水泵输出滤波器输出 | water_filter_output | simulation_water_filter_output | water_filter_output | controller_output
true_load |  |  |  | physical_process | observable state | true_load | true_load | true_load | state
coal_flow |  |  |  | physical_process | observable state | coal_flow | coal_flow | coal_flow | state
feedwater_flow |  |  |  | physical_process | observable state | feedwater_flow | feedwater_flow | feedwater_flow | state
main_steam_flow |  |  |  | physical_process | observable state | main_steam_flow | main_steam_flow | main_steam_flow | state
waterwall_temp |  |  |  | physical_process | observable state | waterwall_temp | waterwall_temp | waterwall_temp | state
main_steam_pressure |  |  |  | physical_process | observable state | main_steam_pressure | main_steam_pressure | main_steam_pressure | state